## Sheet1
[9 empty] | Fan Laws | [6 empty] | Capacitors
Calculate ▲T (Temperature drop/rise through the heat exchanger). | [8 empty] | Fan Law 1. | [6 empty] | In Parallel-Add Capacitors together, Volts = lowest rated capacitor.
▲T | = | BTU/H | / | CFM |  |  |  |  | New CFM= (new rpm x existing cfm)/existing rpm | [6 empty] | New µf | = | Cap1 µf | Cap2 µf | Cap3 µf
65.5864 |  | 85000 | / | 1200 | 1.08 x CFM (Typical) |  |  |  | New RPM=(new cfm X existing rpm) / existing cfm | [6 empty] | 27.5 |  | 5 | 10 | 12.5
[16 empty] | New Volts= |  | 330 | 440 | 333
Airflow when you know the ▲T, CFM=BTU/h / (1.08 x ▲T). | [8 empty] | New CFM | = | Existing RPM |  | Existing CFM |  | New RPM | 330 |  | Cap1 Volts | Cap2 Volts | Cap3 Volts
CFM | = | BTU/H | / | (1.08 x ▲T) |  |  |  |  | 1200 |  | 825 |  | 1000 |  | 990
1124.3386 |  | 85000 | / | 70 | [11 empty] | In Series, µf will be lower, Volts are added together.
[9 empty] | New RPM= |  | Existing CFM |  | Existing RPM |  | New CFM | New µf | = | Cap1 µf | Cap2 µf | Cap3 µf
Airflow required when you know the furnace output and | [8 empty] | 990 |  | 1000 |  | 825 |  | 1200 | 7.1591 |  | 35 | 15 | 22.5
size of evaporator coil. Size ductwork to larger CFM. | [15 empty] | New Volts= |  | 330 | 440 | 333
Heating CFM | = | BTU/H | [6 empty] | Fan Law 2. | [6 empty] | 1103 |  | Cap1 Volts | Cap2 Volts | Cap3 Volts
1190 |  | 85000 | @ | 14 | 14 CFM/1000 BTU/h (Typical) |  |  |  | Static Pressure
New s.p=existing s.p x (new RPM/existing RPM)^2
Cooling CFM | = | Tons |  | CFM/Ton
1600 |  | 4 | @ | 400 | 400 CFM/Ton (Typical) |  |  |  | New Static Pressure | = | Exist S.P. |  | Existing RPM |  | New RPM
[9 empty] | 0.72 |  | 0.5 |  | 825 |  | 990
Total Sensible Heat. |  | Compare Total Sensible Heat to Furnace BTU intput.
Calculate thermal efficiency. | [8 empty] | Fan Law 3.
TSH | = | CFM | X | ▲T |  |  |  |  | Horsepower
55080 |  | 850 | X | 60 | CFM X 1.08 x ▲T |  |  |  | New hp=existing hp x (new RPM/existing RPM)^3
| Furnace BTU Input | 80000 |  | 68.85% | Total System Efficiency |  |  |  | New Horsepower | = | Existing HP |  | New RPM |  | Existing RPM
[9 empty] | 0.57024 |  | 0.33 |  | 990 |  | 825
Calculate CFM from Pressure.
|  | Static |  |  |  |  | Duct |  | Pulley fan RPM
(Rect. Duct) CFM |  | (Return Port) |  | Ft/min |  | Lenth (in) |  | Width (in) |  |  | Diameter of |  | Diameter of
1298.5787 |  | 0.0545 |  | 934.9767 |  | 20 |  | 10 | Fan RPM | = | Fan Pulley |  | Motor Pulley |  | Motor RPM
(Round Duct) CFM |  | Static |  | Ft/min |  | Diam (in) |  |  | 739.2857 |  | 7 |  | 3 |  | 1725
1152.6402 |  | 0.055 |  | 939.2558 |  | 15
[9 empty] | CFM-Electric Heat | [5 empty] | (3.4141BTU/Watt)
Adjusted CFM for Temperature and Altitude. | [8 empty] | CFM | = | Volts | X | Amps | X | ▲T
Adjusted CFM |  | CFM (above) |  | AD Corr Factor |  | Temp (F°) |  | Alt. (Feet) | 1168.5164 |  | 230 |  | 45 |  | 28
1550.2858 |  | 1299 |  | 0.83791 |  | 150 |  | 1000
Misc. Scratch Pad-doesn't affect above calculations
PRESSURE = TOTAL-STATIC, THEN SQRT OF PRESSURE x 4005 x SQFT OF DUCT (FT LENGTH X FT WIDTH) OR pi*RADIUS^2
5.2556 | Alternate constant |  |  | 5.2561 |  | Standard constant
temp & pressure calc
0.77871
0.77871